## Tech - Specs
DV 10 powered 500 kVA Gen-set
Technical specifications
GENSET PARAMETERS
Genset Model |  | KG500WS3
KVA Rating at 0.8 P.F. | kVA | 500
KW Rating 0.8 P.F. | kW | 400
Voltage | V | 415
Frequency | Hz | 50
Phase |  | 3
Power factor |  | 0.8
Overall Dimensions (For canopied genset)(LXWXH) | mm
L |  | 6200
W |  | 2000
H |  | 2570*
H1 |  | 3285**
Approximate Dry Weight (with canopy) | Kg | 6655
Genset static load (Max) | Kg | 7602.75
Rated speed | RPM | 1500
Method of Starting |  | Electric (24V)
Governing class (According to ISO 8528-Part2) |  | G3
Overload capability (for 1hr in 12 hrs operation) | % | 10
Fuel consumption at 75% load | Ltr/Hr | 79.18***
Lube Oil Consumption % of fuel consumption | % | 0.12^
Lube oil change period | Hrs | 500
Alternator efficiency at 75% load | % | 95.3
DG set Noise level at 1Mtr (with canopy) | dBA | 75
Overall thermal effiency of engines/break thermal effiency of engines at 100%load | % | 44.1171
Mechanical effiency 100% load | % | 90
ENGINE DATA
Engine model |  | DV 10
Rated output (prime power rating as per ISO 3046) | kW ( hp ) | 447.5 (608)
No. of cylinders | No. | 10
Engine configuration (Inline / V type) |  | V type
Operating cycle |  | 4 stroke DI
Displacement | Ltrs | 19.9074
Bore x Stroke | mm | 130 x 150
Aspiration |  | TA
Compression Ratio |  | 16.5 : 1
Piston speed | m/s | 7.5
Brake Mean Effective Pressure (BMEP) | Kg/cm2 | 17.98
Firing order (Starting from gear end) |  | 1-6-5-10-2-7-3-8-4-9
Overall dimension (Length x Width x Height) | mm | 1793 x 1125 x 1410
Block loading capacity (as per ISO 3046-Part4) | % | 45
Engine weight (Dry weight of bare engine) | Kg | 1840
FUEL SYSTEM
Type |  | Inline
Static Injection timing | Deg BTDC | 16(+/-1)
Injectors hole Nos. x Size | mm | 7 X 0.248mm
Fuel oil |  | HSD IS 1460
Fuel Filter type |  | Spin on
Filtration capacity | Micron | 5
Fuel transfer line restriction (maximum allowable) | KPa | 100
Fuel transfer pump pressure | Kpa | 250
Max lift of fuel transfer pump | m | 1
Nozzle opening pressure | Kg/cm2 | 260
Specific Fuel Consumption at
50% load | (g/Hp-hr) | 150^^
75% load | (g/Hp-hr) | 146^^
100% load | (g/Hp-hr) | 143^^
LUBE OIL SYSTEM
Recommended lube oil |  | K Oil Super
Lube oil pump |  | G Rotor pump
Lube oil sump capacity(Max) | Ltr | 45
Lube oil sump capacity(Min) | Ltr | 40
Lube oil system capacity | Ltr | 50
Angularity Limit of oil sump(along or across crankshaft axis) | Deg | 15
Lube oil Pressure range at rated load | bar | 4 to 4.5
Lube oil filter type |  | Spin-on
Filtration capacity | Micron | 12
Lube oil pump flow rate(At 2935 rpm with 3.5bar pressure) | LPM | 130
Lube oil change period | Hrs | 500^^^
COOLING SYSTEM
Type of cooling |  | Liquid cooled
Engine coolant flow rate | LPM | 700
Coolant pressure | Kg/cm2 | 1
Radiator Cooled:
Qty of coolant (Engine) | Ltr | 36
Qty of coolant (Radiator) | Ltr | 94
Total qty of coolant (including pipings) | Ltr | 133
K-Cool super | Ltr | 50:50
Cooling/Ventilation Air flow through canopy | m3/min | 907.2
Combustion Air inlet flow | m3/min | 51.2117
Total Fresh Air required | m3/min | 958.4117
Heat Exchanger cooled:
Qty of coolant (HE + CAC + pipings) | Ltr | 65
Raw water Flow rate across Heat exchanger | LPM | 370
Raw water Flow rate across CAC | LPM | 210
Raw water pressure | Kg/cm2 | 2
Ventilation Air Flow required to carry out radiated heat in case of Acoustic enclosure installations | m3/min | 645
Operating Temperature range of the Thermostat | Deg C | 74 to 88
Maximum Coolant temp allowed | Deg C | 104
HEAT REJECTION DETAILS
Heat Rejection to coolant | kW | 213.5
Heat Rejection to CAC | kW | 86.9
Heat Rejection to exhaust | kW | 286.4
Heat Rejection from engine surface | kW | 72.77
AIR INTAKE SYSTEM
Intake filter type |  | Dry
Dirty element restriction | mm of Wg | 635^^^^
Intake manifold pressure | KPa | 294
Maximum Intake manifold temperature(at Altitude 1000m & at temp 45 deg) | Deg C | 74.36
EXHAUST SYSTEM
Exhaust silencer type |  | Residential/Hospital grade
Exhaust noise level (with Silencer) @ 1M | dBA | <75
Max. Permissible exhaust back pressure | mm of H2O (kpa) | 1172(25)
Exhaust gas flow | kg/hr | 2517
Exhaust gas temperature (Max ) | Deg C | 600
Exhaust Smoke level at 100% load(at NTP condition) | BSU | 2
Min exhaust gas pipe size (per bank)(diameter) | mm | 106
GOVERNER DATA
Type |  | Electronic: Integral with FIP & Isochronous capability
Whether adjustable droop provided |  | yes
Transient speed increase for sudden 100% decrease of load | % | 10
Transient speed decrease for permissible sudden increase of load | % | 10
Recovery time | sec | 8
Speed raise / lower from panel provided |  | yes
VALVE MECHANISM
Type |  | OHV
Valve clearance at cold: Inlet / Exhaust | mm | 0.35
Valve Timing: Inlet open / Inlet close | Deg | 1deg 27minBTDC/ 11deg 27minABDC
Exhaust open / exhaust close | Deg | 24deg43min BBDC 7deg18minBTDC
OTHER INFORMATION
Maximum time to start from cold & attain rated Speed & ready to take load | Sec | 5
Overload capacity | % | 10% for 1hr in 12hrs of Operation
* Height of genset excluding silencer
** Height of genset including silencer
*** Considering Specific gravity of diesel as 0.845(+5% tolerance applicable as per ISO 3046)
^ Average value ,subject to use of recommended K-oil as lubrication oil.
^^ Declared sfc for well run engine tested at standard conditions(+5% tolerance applicable as per ISO 3046)
^^^ First oil change at 50hrs
^^^^Do the maintenance of air cleaner element depends on Restriction indicator showing red band or 635 mm of wg pressure whichever will be earlier